## Consolidated Checklist
Site Name | Unit |  | Facility-Wide | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
NVA01A | Monitoring Device | Hour meter | X
Catalyst bed temp | bar: 1; 3 to 7; 9
Urea consumption | bar: 1; 3 to 7; 9
Electrical KiloWatt (kWe) output | bar: 10 to 12
| Operating Limit | 200 hour (hr)/rolling 12-months | bar: 1 to 9
300 hr/rolling 12-months | bar: 13 to 17
400 hr/rolling 12-months | bar: 10 to 12
100 hr/year (yr) Maintenance and Readiness Testing (MCRT) | bar: 1 to 9
36 hr/yr MCRT | bar: 10 to 17
50 hr/rolling 12-months uncontrolled operation | bar: 1; 3 to 7; 9
No MC/RT operations 7:00 a.m.–5:00 p.m., May 1–Sept 30 | bar: 10 to 17
|  | Ultra-Low Sulfur Diesel (ULSD) only | X
20% Visible Emissions (VE) & 6 minutes (min)/hr <30% max | bar: 1 to 9
5% VE & 6 min/hr <10% max | bar: 10 to 17
Startup/shutdown 10% & 6 min/hr <20% total | bar: 10 to 17
2,000 kWe max output | bar: 10 to 12
| Initial Compliance | Two of three units stack-tested within 120 days of integration start | bar: 10 to 12
Two of five units stack-tested within 120 days of integration start | bar: 13 to 17
Method 9 completed or conducted concurrently with stack testing | bar: 10 to 17
kWe Meter testing completed or conducted concurrently with stack testing | bar: 10 to 12
Two copies of stack test and Visible Emissions Evaluation (VEE) reports due to VADEQ within 60 days of testing | bar: 10 to 17
VADEQ notified 30 days before stack test and documented approval | bar: 10 to 17
| On-Site Records | Tier 2 engine certification documentation | X
|  | 12-month rolling record of operating hours | X
|  | Reason for every operation | X
MCRT hours and dates | bar: 10 to 17
Hours of uncontrolled operation | bar: 1; 3 to 7; 9
Amount of urea consumed | bar: 1; 3 to 7; 9
|  | U.S. EPA Certificates of Conformity for all engines kept on-site | X
Engine operation manuals kept on-site
|  | Enine manufacturer specifications kept on-site | X
Logs of kWe output meter | bar: 10 to 12
|  | Documentation of malfunctions lasting more than one hour, including: | X
|  | (a) Date of malfunction | X
|  | (b) Time of malfunction | X
|  | (c) Duration of malfunction | X
|  | (d) Description of malfunctions including: | X
i - Which unit
ii - Pollutant(s) affected
iii - Cause of malfunction
|  | (e) Corrective action take to remedy malfunction | X
|  | Permit is maintained on-site | X
Log date/time and reason for May 1-Sept 30 operation | bar: 10 to 17
| Notifications | Initial Construction Notification: Submit within 30 days and include the following: | bar: 10 to 17
(a) Building | bar: 10 to 17
(b) Unit reference number of the initial unit installed at each building | bar: 10 to 17
(c) Date installation commenced | bar: 10 to 17
VADEQ notified prior to Selective Catalytic Reduction (SCR) maintenance | bar: 1; 3 to 7; 9
Malfunction reported to VADEQ within four daytime hours of discovery of condition
|  | Written malfunction documentation reports sent to VADEQ within 14 days of discovery of condition | X
Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | bar: 10 to 17
Site Name | Unit |  | Facility-Wide | EG-01 | EG-02 | EG-03 | EG-04 | EG-05 | EG-06 | EG-07 | EG-08 | EG-09 | EG-10 | EG-11 | EG-12 | EG-13 | EG-14 | EG-15 | EG-16 | EG-17 | EG-18 | EG-19 | EG-20 | EG-21 | EG-22 | EG-23 | EG-24 | EG-25 | EG-26 | EG-27 | EG-28 | EG-29 | EG-30 | EG-31 | EG-32 | EG-33 | EG-34 | EG-35 | EG-36 | EG-37 | EG-38 | EG-39 | EG-40 | EG-41 | EG-42 | EG-43 | EG-44
NVA02D/ NVA02E | Monitoring Device | Non-resettable hour meter | X
| Maintenance and Commissioning/Readiness Testing (MC/RT) Operating Limits | No MC/RT operations 7:00 am-5:00 pm, May 1-Sept 30 | X
|  | Scheduled MC/RT limited to 18 hours per 12-month rolling period | X
500 hour/12-month rolling period for all operating categories
| General Operating Limits | 3,390 hour/12-month rolling period for all purposes combined | X
|  | 5% Visible Emissions (VE) for the first six minutes of each operating period and less than 10% VE max for remaining time in each operating period | X
|  | Ultra Low Sulfur Diesel (ULSD) and Hydrotreated Vegetable Oil (HVO) are the only permitted fuels | X
|  | 5% VE for the first six minutes after start-up and less than 20% VE max for shutdown in each operating period | X
| Initial Compliance | Five units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration start (1 >CAT, > 1 Kohler) | bar: EG-01 to EG-42
NOX & CO stack tested within 120 days of integration start | bar: EG-43
Visible Emissions Evaluation (VEE) was conducted concurrently with initial stack testing | bar: EG-01 to EG-43
VADEQ notified 30 days before stack test and documented approval | bar: EG-01 to EG-43
Two copies of stack test and VEE reports due to VADEQ within 60 days of testing | bar: EG-01 to EG-43
| On-Site Records | U.S. EPA Certificates of Conformity for all engines kept on-site | X
|  | Engine information documented: make, model, serial number, model year, max engine power, engine displacement | X
Manufacturer's written operating instructions
Operating Log containing the following for every operation:
(a) Date of Operation
(b) Reason for operation
(c) Start time of operation
(d) End time of operation
(e) Starting hour meter reading
(f) Ending hour meter reading
(g) Was visible smoke observed
|  | Monthly/annual total hours of operation | X
|  | Monthly/annual hours of MC/RT operation | X
|  | Monthly/annual combined total hours of operation | X
|  | Fuel supplier certifications showing fuel contains less than 15 parts per million (ppm) Sulfur | X
|  | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | X
|  | MC/RT (scheduled & unscheduled) records and operator trainings | X
|  | Results of all stack tests and VEEs | X
|  | Changes in settings permitted by manufacturer | X
|  | For each integration-period operation, retain: forecasted and measured ozone AQI, any air alerts, and commissioning meter readings (hours and run duration) | X
Documentation of malfunctions lasting more than one hour, including:
(a) Date of malfunction
(b) Time of malfunction
(c) Duration of malfunction
(d) Description of malfunctions including:
Which unit
Pollutant(s) affected
Cause of malfunction
|  | (e) Corrective action taken to remedy malfunction | X
| Notifications to Viginia Department of Environmental Quality (VADEQ) | Initial Construction Notification - Submit within 30 days and include the following:
(a) Building
(b) Unit reference number of the initial unit installed at each building
|  | (c) Date installation commenced | X
|  | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and integration operational period start and end) | X
|  | No later than 14 business days after a malfunction causing excess emissions for more than one hour is discovered | X
|  | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery | X
Site Name | Unit |  | Facility-Wide | DEG-01 | DEG-02 | DEG-03 | DEG-04 | DEG-05 | DEG-06 | DEG-07 | DEG-08 | DEG-09 | DEG-10 | DEG-11 | DEG-12 | DEG-13 | DEG-14 | DEG-15 | DEG-16 | DEG-17 | DEG-18 | DEG-19 | DEG-20 | DEG-21 | H-1
NVA05D | Monitoring Device | Non-resettable hour meter | X
kWe output monitor
| MC/RT Operation | No MC/RT operations 7:00 am-5:00 pm, May 1-Sept 30
Scheduled MC/RT limited to 18 hours per 12-month rolling period
21 hours per calendar year of MC/RT operation
| Operating Limits | 1,680 hour/12-month rolling period for combined operation of EGENs DEG-01 through DEG-21
500 hour/12-month rolling period for each individual generator within the 1,680 hr/ 12-month rolling period sitewide limit
80 hour/12-month rolling period for EGEN H-1
5% Visible Emissions (VE) for the first six minutes of each operating period and less than 10% VE max for remaining time in each operating period
ULSD is the only permitted fuel
5% VE for the first six minutes after start-up and less than 20% VE max for shutdown in each operating period
Maximum electrical output for EGEN H-1 is 940 kWe
500 hour/rolling 12-months | bar: DEG-01 to DEG-21
80 hour/rolling 12-months | bar: H-1
|  | 21 hour/yr MCRT | X
|  | No MC/RT operations 7:00 am-5:00 pm, May 1-Sept 30 | X
| Initial Compliance | Four of 21 units (DEG-01 through DEG-21) stack-tested within 120 days of integration start | bar: DEG-01 to DEG-21
Method 9 completed or conducted concurrently with stack testing | bar: DEG-01 to DEG-21
kWe meter testing | bar: H-1
Two copies of stack test and Visible Emissions Evaluation (VEE) reports due to VADEQ within 60 days of testing | bar: DEG-01 to DEG-21
VADEQ notified 30 days before stack test and documented approval | bar: DEG-01 to DEG-21
| On-Site Records | U.S. EPA Certificates of Conformity for all engines kept on-site | X
|  | Engine information documented: make, model, serial number, model year, max engine power, engine displacement | X
|  | Manufacturer's written operating instructions | X
|  | Operating Log containing the following for every operation: | X
|  | (a) Date of Operation | X
|  | (b) Reason For operation | X
|  | (c) Start time of operation | X
|  | (d) End time of operation | X
|  | (e) Starting hour meter reading | X
|  | (f) Ending hour meter reading | X
(g) Was visible smoke observed
Monthly/annual total hours of operation
Monthly/annual hours of MC/RT operation
Monthly/annual combined total hours of operation
Fuel supplier certifications showing fuel contains less than 15 parts per million (ppm) Sulfur
Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5
MC/RT (scheduled & unscheduled) records and operator trainings
Results of all stack tests and VEEs
Changes in settings permitted by manufacturer
For each integration-period operation, retain: forecasted and measured ozone AQI, any air alerts, and commissioning meter readings (hours and run duration)
Documentation of malfunctions lasting more than one hour, including:
(a) Date of malfunction
(b) Time of malfunction
(c) Duration of malfunction
(d) Description of malfunctions including:
Which unit
|  | Pollutant(s) affected | X
|  | Cause of malfunction | X
(e) Corrective action taken to remedy malfunction | bar: DEG-01 to DEG-21
|  | Changes in settings permitted by manufacturer | X
Results of electrical power output control device validation demonstrations | bar: H-1
|  | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | X | bar: DEG-02
|  | Inventory of spare parts | X
| Notifications | Initial Construction Notification - Submit within 30 days and include the following: | X
|  | (a) Building | X
|  | (b) Unit reference number of the initial unit installed at each building | X
|  | (c) Date installation commenced | X
Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and integration operational period start and end)
No later than 14 business days after a malfunction causing excess emissions for more than one hour is discovered
Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think we need to expand on what this means a little bit/provide context
Note on C27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is demonstrated by the CoCs according to Rob
Note on B48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think we can clean up all 4 of these to be more concise/specific
Note on C48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I would recommend adding to the unit ref. number “of the initial unit installed”; technically, u only have to mention the initial one and not the rest in that building. We could rephrase this one to say “Initial Notification: Submit within 30 days and include the following xyz” but up to you. Reply: Left in this row since it needs to be added for certain units
Note on N48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is listed in the permit as being required for 10-17 - they may have completed this but if we are doing an audit we will want to know so we can check for the proof of submitted records.
Note on C54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Missing comma between date and time; We should add more detail to this one as its more than one hour malfunction; missing no later than 4 daytime business hours after discovered condition
Note on C55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Left in this row since it needs to be added for certain units
Note on N55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See permit page 15

## NVA01A (hidden)
Site | Registration No. | Unit ID | Make | Model | kWe | Derated kWe | bhp | Last Permit Date | Controls | Monitor Dev 1 | Monitor Dev 2 | Monitor Dev 3 | Monitor Dev 4 | Operating Limit 1 | Operating Limit 2 | Operating Limit 3 | Operating Limit 4 | Operating Limit 5 | Operating Limit 6 | Operating Limit 7 | Operating Limit 8 | Operating Limit 8 | Initial Compliance 1 | Initial Compliance 2 | Initial Compliance 3 | Initial Compliance 4 | Initial Compliance 5 | Records Onsite 1 | Records Onsite 1 | Records Onsite 2 | Records Onsite 3 | Records Onsite 4 | Records Onsite 5 | Records Onsite 6 | Records Onsite 7 | Records Onsite 8 | Records Onsite 9 | Records Onsite 10 | Notifications 1 | Notifications 2 | Notifications 3 | Notifications 4 | Notifications 5 | Notifications 6 | Notifications 7
NVA01A | 74079 | 1 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 2 | CAT | 3516A | 1750 | -- | 2304 | 2015 | -- | Hours Meter | -- |  | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | -- | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | -- | -- | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 3 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 4 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 5 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 6 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 7 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 8 | CAT | 3516A | 1750 | -- | 2304 | 2015 |  | Hours Meter | -- | -- | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | -- | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- |  |  | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 9 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 10 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 11 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 12 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 13 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 14 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 15 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 16 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 17 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
Note on E11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DQKAN
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3,585 bhp - I would recommend adding an additional column for the de rated bhp of 2,854

## NVA02D
Site | Registration No. | Unit ID | Make | Model | kWe | Derated kWe | bhp | Last Permit Date | Controls | Monitor Dev 1 | Monitor Dev 2 | Monitor Dev 3 | Monitor Dev 4 | Operating Limit 1 | Operating Limit 2 | Operating Limit 3 | Operating Limit 4 | Operating Limit 5 | Operating Limit 6 | Operating Limit 7 | Operating Limit 7 | Operating Limit 8 | Initial Compliance 1 | Initial Compliance 2 | Initial Compliance 3 | Initial Compliance 4 | Initial Compliance 5 | Records Onsite 1 | Records Onsite 2 | Records Onsite 3 | Records Onsite 4 | Records Onsite 5 | Records Onsite 6 | Records Onsite 7 | Records Onsite 8 | Records Onsite 9 | Records Onsite 10 | Records Onsite 11 | Records Onsite 12 | Records Onsite 13 | Records Onsite 14 | Records Onsite 15 | Records Onsite 16 | Records Onsite 17 | Notifications 1 | Notifications 2 | Notifications 3 | Notifications 4 | Notifications 5 | Notifications 6 | Notifications 7 | Notifications 8 | Notifications 9
NVA02D | 74224 | EG-01 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-02 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-03 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-04 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-05 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-06 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-07 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-08 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-09 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-10 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-11 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-12 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-13 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-14 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-15 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-16 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-17 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-18 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-19 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-20 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-21 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-22 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-23 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-24 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-25 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-26 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-27 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-28 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-29 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-30 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-31 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-32 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-33 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-34 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-35 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-36 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-37 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-38 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-39 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-40 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-41 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-42 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-43 | Caterpillar | C32 | 1,250 | N/A | 1,821 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | Stack tested for NOX & CO within 120 days of integration beginning | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-44 | Caterpillar | C32 | 1,000 | N/A | 1,438 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery

## NVA05D
Site | Registration No. | Unit ID | Make | Model | kWe | Derated kWe | bhp | Last Permit Date | Controls | Monitor Dev 1 | Monitor Dev 2 | Monitor Dev 3 | Monitor Dev 4 | Operating Limit 1 | Operating Limit 2 | Operating Limit 3 | Operating Limit 4 | Operating Limit 5 | Operating Limit 6 | Operating Limit 7 | Operating Limit 7 | Operating Limit 8 | Initial Compliance 1 | Initial Compliance 2 | Initial Compliance 3 | Initial Compliance 4 | Initial Compliance 5 | Records Onsite 1 | Records Onsite 1 | Records Onsite 2 | Records Onsite 3 | Records Onsite 4 | Records Onsite 5 | Records Onsite 6 | Records Onsite 7 | Records Onsite 8 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 9 | Records Onsite 10 | Notifications 1 | Notifications 1 | Notifications 1 | Notifications 2 | Notifications 3 | Notifications 4 | Notifications 5 | Notifications 6 | Notifications 7
NVA05D | 74246 | DEG-01 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-02 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-03 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-04 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-05 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-06 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-07 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-08 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-09 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-10 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-11 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-12 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-13 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-14 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-15 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-16 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-17 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-18 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-19 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-20 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-21 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | H-1 | Rehlko | KD1250 | 1250 | 940 | 1865 | 2025 | -- | Hours Meter | -- | -- | kWe Output | 80 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 940 kWe Max Output | -- | -- | -- | kWe Meter testing | -- | -- | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | -- | Results of electrical power output control device validation demonstrations | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership

## All Data Pivot
Count of Unit ID | Site | [5 empty] | Site
Records Onsite 11 | NVA01A | NVA02D | NVA05D | (blank) | Grand Total |  | NVA01A | NVA02D | NVA05D | (blank) | Grand Total
-- |  |  | 1 |  | 1 | Count of Unit ID | 17 | 44 | 22 |  | 83
MC/RT (scheduled & unscheduled) records and operator trainings |  | 44 |  |  | 44
Permit kept on site | 17 |  |  |  | 17
Results of all stack tests and VEEs |  |  | 21 |  | 21
(blank)
Grand Total | 17 | 44 | 22 |  | 83

## All Data
Site | Registration No. | Unit ID | Make | Model | kWe | Derated kWe | bhp | Last Permit Date | Controls | Monitor Dev 1 | Monitor Dev 2 | Monitor Dev 3 | Monitor Dev 4 | Operating Limit 1 | Operating Limit 2 | Operating Limit 3 | Operating Limit 4 | Operating Limit 5 | Operating Limit 6 | Operating Limit 7 | Operating Limit 8 | Operating Limit 9 | Initial Compliance 1 | Initial Compliance 2 | Initial Compliance 3 | Initial Compliance 4 | Initial Compliance 5 | Records Onsite 1 | Records Onsite 2 | Records Onsite 3 | Records Onsite 4 | Records Onsite 5 | Records Onsite 6 | Records Onsite 7 | Records Onsite 8 | Records Onsite 9 | Records Onsite 10 | Records Onsite 11 | Records Onsite 12 | Records Onsite 13 | Records Onsite 14 | Records Onsite 15 | Records Onsite 16 | Records Onsite 17 | Records Onsite 18 | Notifications 1 | Notifications 2 | Notifications 3 | Notifications 4 | Notifications 5 | Notifications 6 | Notifications 7 | Notifications 8 | Notifications 9
NVA01A | 74079 | 1 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 2 | CAT | 3516A | 1750 | -- | 2304 | 2015 | -- | Hours Meter | -- |  | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | -- | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | -- | -- | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 3 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 4 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 5 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 6 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 7 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 8 | CAT | 3516A | 1750 | -- | 2304 | 2015 |  | Hours Meter | -- | -- | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | -- | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- |  |  | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 9 | CAT | 3516A | 1750 | -- | 2304 | 2015 | SCR | Hours Meter | Catalyst Bed Temp | Urea Consumption | -- | 200 hr/rolling 12- months | 100 hr/yr MCRT | 50 hr/rolling 12- months uncontrolled operation | ULSD Only | 20% VE & 6 min/hr <30% max | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Record of hours of operation 12 month rolling | Reason for Operation | -- | Hours of uncontrolled operation | Amount of urea consumed | CoC, Operation manuals, engine specs | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | Prior notice to VADEQ of SCR maintenance | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 10 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 11 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 12 | Cummins | -- | 2500 | 2000 | -- | 2020 | -- | Hours Meter | -- | -- | kWe Output | 400 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 2,000 kWe Max Output | -- | 2 of 3 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | kWe Meter testing concurrent with stack testing | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | kWe output meter logs | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 13 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 14 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 15 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 16 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA01A | 74079 | 17 | CAT | -- | 3500 | -- | 4393 | 2021 | -- | Hours Meter | -- | -- | -- | 300 hr/rolling 12-months | 36 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | -- | 2 of 5 units stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | -- | Record of hours of operation 12 month rolling | Reason for Operation | MCRT Hours and dates | -- | -- | CoC, Operation manuals, engine specs | -- | records of operation in ozone season (1 May - 30 Sept.) | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | -- | -- | -- | -- | -- | -- | Malfunctions (date time, duration, description, & corrective actions taken) reports sent to VADEQ within 14 days of discovery | -- | -- | -- | --
NVA02D | 74224 | EG-01 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-02 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-03 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-04 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-05 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-06 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-07 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-08 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-09 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-10 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-11 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-12 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-13 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-14 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-15 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-16 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-17 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-18 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-19 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-20 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-21 | Caterpillar | C175-16 | 3,000 | N/A | 4,423 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-22 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-23 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-24 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-25 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-26 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-27 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-28 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-29 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-30 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-31 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-32 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-33 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-34 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-35 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-36 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-37 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-38 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-39 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-40 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-41 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-42 | Caterpillar or Kohler | C175-16 or KD3000 | 3,000 | N/A | 4,423 or 4,332 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | 5 units (EG-01 through EG-42) stack tested for NOX & CO within 120 days of integration beginning - must include at least one of each type of engine (CAT & Kohler) | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-43 | Caterpillar | C32 | 1,250 | N/A | 1,821 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | Stack tested for NOX & CO within 120 days of integration beginning | VEE concurrent with initial stack testing | Stack testing and VEE protocol due to VADEQ at least 30 days prior | Two copies of stack test and VEE reports due to VADEQ within 60 days after test | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA02D | 74224 | EG-44 | Caterpillar | C32 | 1,000 | N/A | 1,438 | October 16, 2023 | N/A | Hour Meter | N/A | N/A | N/A | 500 hr/12-month rolling period for all purposes individually | 3,390 hr/12-month rolling period for all purposes combined | 18 hr/12-month rolling period for Scheduled MC/RT individually | No operation for MC/RT between 7 am and 5 pm during May 1 through September 30 | ULSD or HVO | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% & 6 min/hr <20% total | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations (hour meter readings) | Manufacturer's written operating instructions | Monthly/annual total hours of operation | Monthly/annual hours of MC/RT operation | Monthly/annual combined total hours of operation | Fuel supplier certifications | Monthly/annual emissions calculations for NOX, CO, VOC, PM10, and PM2.5 | Stack test and VEE results | MC/RT (scheduled & unscheduled) records and operator trainings | Changes in settings permitted by manufacturer | Reasons for operation w/ date, cause of operation/emergency, ISO-declared emergency notification, and hours of operation | Date, time, and reason for operation that occured between May 1 and September 30 | Forecasted and measured ozone AQI when engine operated during integrational operational period, air alerts for the days of operation, and commissioning hours meter readings and duration | Malfunction, shutdown, or failure that results in excess emissions for more than one hour |  |  | Installation commencement notification within 30 days (including name and address, building, unit ref. number, and date installation commenced) | Start and end of integration operational period within 15 days of the last generator at each building's completion (including unit ref. number, engine information, installation date, and inegration operational period start and end) | No later than 4 business days after a malfunction causing excess emissions for more than one hour is discovered | Written description of any malfunction causing excess emissions over one hour within 14 days of discovery
NVA05D | 74246 | DEG-01 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-02 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-03 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-04 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-05 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-06 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-07 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-08 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-09 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-10 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-11 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-12 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-13 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-14 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-15 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-16 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-17 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-18 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-19 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-20 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | DEG-21 | Rehlko | KD3000 | 3000 | -- | 4332 | 2025 | -- | Hours Meter | -- | -- | -- | 500 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | -- | 1,680 hr rolling 12-months combined (DEG-01 through DEG-21) | 4 of 21 units (DEG-01 through DEG-21) stack tested within 120 days of integration beginning | Method 9 concurrent with stack testing | -- | VADEQ 30 day prior notification of stack test & approval | 60 days for stack test results to VADEQ | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | Results of all stack tests and VEEs | -- | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership
NVA05D | 74246 | H-1 | Rehlko | KD1250 | 1250 | 940 | 1865 | 2025 | -- | Hours Meter | -- | -- | kWe Output | 80 hr/rolling 12- months | 21 hr/yr MCRT | -- | ULSD Only | 5% VE & 6 min/hr <10% max | Startup/shutdown 10% 6min/hr <20% total | No MCRT operation in ozone Season (1 May -30 Sept) | 940 kWe Max Output | -- | -- | -- | kWe Meter testing | -- | -- | Documentation that engine is Tier 2 certified | Engine information (make, model, serial number, model year, max. engine power, engine displacement | Log of monitoring device observations | Manufacturer's written operating instructions | Reasons for operation | Times, dates, and reasons for operation within ozone season | AQI forecasts and measurements during integrational operational period | Record of hours of operation 12 month rolling | Monthly and 12 month rolling emissions calculations | Fuel supplier certifications | -- | Results of electrical power output control device validation demonstrations | Records of scheduled and unscheduled maintenance | Records of operator training | Inventory of spare parts | Changes in settings permitted by manufacturers | Malfunctions (date time, duration, description, & corrective actions taken) | Permit kept on site | -- | -- | Date of installation | Start and end dates of integration operational period | Malfunction of control equipment | Change of ownership