| Section 01 MOP Information |  | Site: | Procedure Type: |  | System: |  |  |  | Equipment System: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | NVA06A | MOP |  | Electrical |  |  |  | Construction Support |  |  |  |  |
|  |  | Review By Date: |  | Equipment CMMS ID: |  |  |  |  |  |  | Level Of Risk MEDIUM |  |  |
|  |  | 3/19/2026 |  | FAM025377 UPS-P3-110-01 - NVA06A |  |  |  |  |  |  |  |  |  |
| Work Order# |  | 177621 |  |  |  |  | Required Parts, Tools and Materials: | MOP, Clipboard, Electrical PPE |  |  |  |  |  |
| MOP Overview: |  | This Method of Procedure (MOP) provides an overview of the steps required to electrically and mechanically isolate UPS P3-110-01, including its associated fire protection systems, in order to facilitate the replacement of its battery cabinets. |  |  |  |  |  |  |  |  |  |  |  |
| Section 02 MOP Supporting Documentation |  | Supporting Documentation |  |  |  |  |  |  |  |  |  |  |  |
| - Critical Facility Work Rules - NVA06A LOTO AP - NVA06A LOTO Log - JSA |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 03 Risk & Safety Requirements |  | Risk and Safety Requirements |  |  |  |  |  |  |  |  |  |  |  |
| - Risks: - A utility power interruption will result in client servers being single-sourced until generator load transfer is complete. - Safety Requirements: - Proper PPE must be worn, and specific items will be listed in the detailed procedure where applicable. - Type and Magnitude: Equipment ID; Type of Energy; Magnitude. 1ULPA4; Electrical; 0.08 cal/cm^2. UPS-P3-110-01; Electrical; 5.07 cal/ cm2. |
| Section 04 Pre-Maintenance Brief |  | Pre-Maintenance Brief |  |  |  |  |  |  |  |  |  |  |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| Personnel who initial for performance of any step in this procedure are to provide their printed name and sample initial. If insufficient space is provided here, enter name and initial in the Comments Section. ________________________________ _______ __________________________________ _______ Controller Printed Name Initials Operator Printed Name Initials |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Notify client Point(s) of Contact (POC) that the procedure is about to begin and what systems the MOP will affect. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Obtain all required approvals before this procedure commences. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Notify Critical Operations Management that work will be commencing and of expected alarms. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Complete Pre-maintenance brief with all qualified and affected personnel, including vendors involved with this procedure. If the procedure lasts longer than a shift, or new personnel become involved with the procedure, stop the work and perform a pre-maintenance brief. The remaining steps will be read aloud with all participating personnel present |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Discuss the controller and operator roles and designate those personnel prior to commencing work. - The Controller is responsible for coordinating LOTO procedure and ensuring all Qualified Persons, including vendors, have added their personal lock and tag. - The Controller is responsible for notification of all qualified, affected, and other employees as appropriate of the planned equipment shutdown, maintenance, and service. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Facility Electrical and Mechanical systems are in a normal lineup. No other work that affects systems in this procedure in progress. Any exceptions have approval from the COM. Document exceptions in the comment section. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Change of state tags on hand if applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - LOTO equipment is on hand if procedure requires LOTO. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - All PPE is on hand, per the JSA, and ready for use prior to commencing the maintenance. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - All tools and parts are on hand and inventoried prior to commencing maintenance. Verify any tools that require calibration have been tested in periodicity. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Discuss communication methods, as necessary. Face to face, email, radio, or telephone. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify Job Safety Analysis is complete, review all hazards and mitigations with all participating personnel. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - All personnel are responsible for safety. If any unsafe action is observed, stop work, and discuss the how to proceed safely. Gross violations of safety will result in stopping work and escalating to the COM prior to performing any further steps. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - No deviation from this procedure will be allowed. If there are discrepancies, escalate to the COM for direction. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - The outcome of each step should be known prior to the action. If unexpected conditions arise during the procedure, stop, evaluate, and escalate as necessary to the COM. If any unexpected condition occurs that does not relate to the procedure, follow backout procedures listed at the end of this MOP. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 05 Detailed Procedure |  | Detailed Procedure |  |  |  |  |  |  |  |  |  |  |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Send an email to NVA06A_SEV3_Alarm@STACKinfra.com stating that work is about to start and to disregard expected alarms. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify Fire System is called out. If not, call BFPE and put Fire System in test until work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Proceed to Fire Riser Room 1126. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - CLOSE Fire riser PA 1-7 Main Control Valve. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - CLOSE Fire riser PA 1-7 Control Valve. NOTE: Fire Riser System for the following rooms are now Isolated. UPS Rooms 1136, 1137, 1138, 1139, 1140, 1141, and 1142. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Apply LOTO. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - LOTO Identifier: ________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Upon Completion of Step, Fire Watch to be established. (See Table 1.1) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Proceed to Room 1119. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Don appropriate PPE for switching. Safety Equipment; Controller Initials; Operator Initials. 4 Cal/cm2 Arc-rated clothing. 4 Cal/cm2 Arc-rated long sleeve shirt and pants or arc-rated coverall or arc flash suit. 4 Cal/cm2 Arc-rated face shield with wraparound protection + balaclava. 0 Class rubber gloves with leather protectors. Hard Hat. Safety glasses or safety goggles. Hearing protection. Leather work shoes. |  |  |
| - Locate Panel 1ULPA4. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Locate and Identify Circuit 32 for Li-ion Tamer 1136,1137,1138. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - OPEN CKT 32 (Lion Tamer 1136, 1137,1138). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Apply LOTO. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - LOTO Identifier: ______________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Lion Tamer associated with P3-110 is now Mechanically and Electrically Isolated. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 1: Toshiba Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Toshiba to check in with STACK Operations. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Proceed to Elec RM 1138 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to verify UPS-P3-110-01-MIB is OPEN and LOTO’d. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to verify UPS-P3-110-01-MOB is OPEN and LOTO’d. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - UPS-P3-110-01-MIB LOTO Identifier:______________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - UPS-P3-110-01-MOB LOTO Identifier:______________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to place LOTO on UPS-P3-110-01-MIB. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Vendor signature for LOTO of UPS-P3-110-01-MIB |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to place LOTO on UPS-P3-110-01-MOB. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Vendor signature for LOTO of and UPS-P3-110-01-MOB.:___________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to Complete Live Dead Live Test. Test Points; Operations Signature; Vendors Signature. Live. A-B. B-C. C-A. A-GND. B-GND. C-GND. Live. |  |  |
| - Toshiba remove battery jumpers from UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba remove battery jumpers from and UPS-P3-110-01-BAT-CAB-2. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to remove EPO cable from UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to remove EPO cable from UPS-P3-110-01-BAT-CAB-2. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba walk down system to confirm ready for removal and remove Toshiba locks |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 2: REI FA Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - REI FA to check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA to verify the FA system is called out. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA to proceed to Stack OPS Room 1115. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA to Locate MAIN FACP Computer Unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA to disable the affected Electrical Room P3-110 Vesda/FA/and Li-ion Tamer devices via MAIN FACP Computer Unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA will move devices and wiring from affected cabinets UPS-P3-110-01-BAT-CAB-2 and place the End of Line Resistor (EOLR) at furthermost device not affected. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA will move devices and wiring from affected cabinet UPS-P3-110-01-BAT-CAB-1 and place the End of Line Resistor (EOLR) at furthermost device not affected. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Walk down system to confirm all effected devices and attachments have been cleared and cabinets are ready for removal. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI to return to panel to ensure no new troubles or supervisory exists. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 3: BFPE Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to verify CLOSED PA-1-7 in riser room 1126 (isolation for UPS-P3-110 Li-ion Tamer sprinklers). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to Verify PA-1-7 is CLOSED and LOTO’d. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE Sprinkler to apply LOTO to PA-1-7. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Vendor Signature for LOTO of PA-1-7:__________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Remove sprinkler head from UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Remove sprinkler head from UPS-P3-110-01-BAT-CAB-2. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to walk down system and confirm battery cabinet is ready for removal. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 4: Vertiv IMS Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - IMS vendor to remove their CAT6 cabling from UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - IMS vendor to remove their CAT6 cabling from and UPS-P3-110-01-BAT-CAB-2. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - IMS vendor to unbolt cabinets. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - VERTIV IMS to walk down system and confirm it is ready for removal. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 5: A&A Removal Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - A&A to check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations and HITT to confirm battery cabinet is ready to remove. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to remove cabinets from UPS room P3-110 and store in storage room in PH4. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 6: A&A Install Scope of work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - A&A to check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to bring new cabinets from building NVA06B through loading dock. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to set battery cabinets in place in UPS Room P3-110. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to confirm with VERTIV and Toshiba they are placed correctly, and no adjustments need to be made. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to torque all connections to land the equipment on the appropriate pedestal. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - A&A to remove all rigging equipment from area. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 7: REI FA Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK OPERATIONS will verify the fire alarm system is called out. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will begin install prior to any other installation in the battery cabinet. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will drill new holes in battery cabinets for entry point for Li-ion tamer communication cable. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will mount new devices on top vent like previous installation. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will pull new communication wire into new devices. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will verify new devices are communicating properly with active system with assistance from BFPE programmers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI will test new devices allowing the Audio/Visual notification appliances to sound and relays to shunt. To ensure system works as fully designed. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Once testing and commissioning are satisfactory, REI will return to the panel to ensure no new troubles or supervisory alerts exist. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 8: Vertiv IMS Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Bolt together cabinets. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - IMS vendor to install their CAT6 cabling. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - VERTIV IMS to walk down system and confirm all work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 9: Toshiba Install Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Proceed to Elec RM 1138. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to verify UPS-P3-110-01-MOB is OPEN with LOTO still applied. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Vendor Signature of LOTO verification: _________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to verify UPS-P3-110-01-MIB is OPEN with LOTO still applied. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Vendor Signature of LOTO verification: _________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to Complete LDL . Test Points; Operations Signature; Vendors Signature. Live. A-B. B-C. C-A. A-GND. B-GND. C-GND. Live. |  |  |
| - Toshiba to install new batteries. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to install battery jumpers. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to install EPO cable. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Toshiba to walk down system and confirm all work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to clean walk newly installed equipment and check for torque marks. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 10: BFPE Scope of Work |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Check in with STACK Operations and HITT. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE Sprinkler riser to be Verified Isolated by LOTO in riser room 1126 for PA 1-7 Control Valve. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Install sprinkler head in new cabinets. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to walk down system and confirm work is completed. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Check out with STACK Operations and HITT to confirm completion. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 11: System Restoration |  |  |  |  |  |  |  |  |  |  |  | Date: |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - STACK Operations, REI FA, and BFPE to verify that the Li-Ion Tamer system associated with P3-110 remains Mechanically and Electrically Isolated. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - P3-110 Li-ion Tamer Mechanical Isolation: Verify PA 1-8 Control Valve is CLOSED and LOTO’d. BFPE Verification of P3-110 Li-ion Tamer Mechanical Isolation:______________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - P3-110 Li-ion Tamer Electrical Isolation: Verify 1ULPA4 #32 is OPEN and LOTO’d. REI FA Verification of P3-110 Li-Ion Tamer Electrical Isolation:________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to escort the REI FA and BFPE vendors to P3-110 (RM 1138).: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to remove sprinkler heads to support battery cabinet swap on the following UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to remove sprinkler heads to support battery cabinet swap on the following UPS-P3-110-01-BAT-CAB-2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to install Rated Sprinkler Plugs on previously removed Sprinkler Heads for UPS-P3-110-01-BAT-CAB-1. NOTE: This is for temporary restoration of system to ensure monitoring in the following rooms during repair. UPS Rooms 1136, 1137, 1138, 1139, 1140, 1141, and 1142. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to install Rated Sprinkler Plugs on previously removed Sprinkler Heads for UPS-P3-110-01-BAT-CAB-2. NOTE: This is for temporary restoration of system to ensure monitoring in the following rooms during repair. UPS Rooms 1136, 1137, 1138, 1139, 1140, 1141, and 1142. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to remove Li-ion Tamer RJ45 connection to affected cabinet UPS-P3-110-01-BAT-CAB-1 and place the EOLR at furthermost device not affected. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to remove Li-ion Tamer RJ45 connection to affected cabinets UPS-P3-110-01-BAT-CAB-2 and place the EOLR at furthermost device not affected. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to remove the EOLR (End of Line Resistors) from affected cabinet UPS-P3-110-01-BAT-CAB-1 . |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to place EOLR (End of Line Resistors) in the unaffected UPS-P3-110-01-BAT-CAB-0 for temporary storage. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to remove the EOLR (End of Line Resistors) from affected cabinet UPS-P3-110-01-BAT-CAB-2 and place in the unaffected UPS-P3-110-01-BAT-CAB-0 for temporary storage. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and BFPE to place the EOLR (End of Line Resistors) in the unaffected UPS-P3-110-01-BAT-CAB-0 for temporary storage. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to verify that BFPE has installed Rated Sprinkler Plug on previously removed Sprinkler Head for UPS-P3-110-01-BAT-CAB-1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to verify that BFPE has installed Rated Sprinkler Plug on previously removed Sprinkler Head for UPS-P3-110-01-BAT-CAB-2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Proceed to Fire Riser Room 1126. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - BFPE to remove LOTO from Fire riser PA 1-7 Control Valve. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to remove LOTO from Fire riser PA 1-7 Control Valve. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - STACK Operations to slowly OPEN Fire riser PA 1-7 Control Valve and monitor for noise and system pressures. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Locate and Identify Nitro Gen Monitoring System Panel. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify Purity is within Tolerance (95%-100%). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify System Pressure has maintained above 16 PSI. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Slowly OPEN Fire riser PA 1-7 Main Control Valve and monitor for noise and system pressures. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify Fire System is called Restored. If not, call BFPE and put Fire System in restored state as work is completed. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - REI FA and STACK Operations to confirm no known issues with FACP associated with UPS-P3-110-01 and UPS-P3-110-02. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Send an email to NVA06A_SEV3_Alarm@STACKinfra.com stating that work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Notify the COM/ACOM work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Notify client Point(s) of Contact (POC) that the work is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Update any new equipment information into CMMS under the equipment tab. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Ensure that any equipment issues identified have had a corrective maintenance work order created. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - MOP supervisor will ensure that all vendors or contractors have cleaned any, and all debris produced as a result of this MOP. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - MOP supervisor will ensure that all required work is complete and satisfactory. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Ensure each step has been initialed and time stamped. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 06 Back-out Procedures |  | Back-out Procedures |  |  |  |  |  |  |  |  |  |  |  |
| Action |  |  |  |  |  |  |  |  |  |  |  | Time | Initials |
| - Back-out procedures will commence immediately if any problem/failure occurs that affects the critical load. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Stop all work. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - If the nature of the problem includes flooding, fire, or threat to personnel safety, take immediate actions to correct. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - MOP supervisor has informed COM immediately with details of problem/failure, actions taken, and recommended corrective actions. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Safely clear all tools and personnel from the work area. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Corrective actions will be taken to restore the equipment and/or critical load with coordination from the COM. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - After all systems are recovered, an evaluation on site will be made to determine if the work will recommence or be rescheduled at a later date. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Work will recommence only with the permission of site management. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 07 MOP Approval | MOP Approvals |  |  |  |  |  |  |  |  |  |  |  |
| Peer Review: | Reviewers Name: Ryan Manuel |  |  |  | Reviewers Title: COT II |  |  |  | Date: 3/23/2026 |  |  |  |
| Management Approval | Approvers Name: N/A |  |  |  | Approvers Title: N/A |  |  |  | Date: 3/23/2020 |  |  |  |
| Section 08 MOP Completion | Sign-off/Completion |  |  |  |  |  |  |  |  |  |  |  |
| MOP Quality Assurance Completion: | MOP Quality Assurance Name: |  |  |  | MOP Quality Assurance Title: |  |  |  | Date: |  |  |  |
| Section 09 MOP Comments | Completion Comments |  |  |  |  |  |  |  |  |  |  |  |

FIRE WATCH TABLE 1.1

| Affected Room | UPS Room 1136 | UPS Room 1137 | UPS Room 1138 | UPS Room 1139 | UPS Room 1140 | UPS Room 1141 | UPS Room 1142 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Time of Fire Watch |  |  |  |  |  |  |  |